## 7.1-FSC Electricals
FINANCIAL SERVICES COMMISSION BUILDING
7.1 : ELECTRICAL INSTALLATION SCHEDULE OF WORKS
Item | Description | Qty | Unit | Rate | Amount (EC$)
Provide all materials, labour and supervision necessary to complete the Works
in all respects, all as specified, shown on the Drawings or as indicated otherwise.
NOTE: All individual sub-sections of each item are to be priced, indicating cost totals for material + labour. All prices are to quoted in Eastern Caribbean Dollars
E1 | a) 415V 400A 3-Pole 22 kAIC Main Utility Transformer L.V. Isolator | 2 | Item
| b) Automatic Transfer Switch - ASCO 300 (or equal aproved) 415V 400A 3-pole 22 kAIC |  | Item
c) 4C x 240mm2 X.L.P.E. Generator Cables- to Contractor's Estimate
| 1. Main Isolator #1 to ATS |  | m
| 2. ATS to generator |  | m
e) ATS to Main Panel 'M'
| f) Main L.V. Distribution Panel 'M' - 415/240V 3-Phase 4-Wire 30-Way 400A B/B 22 kAIC c/w Digital Power Meter, CT.s, Ground Fault and 250 kA TVSS and all branch circuit breakers |  | Item
| g) Cable Trays, ducts, supports etc. |  | Item
SUB-TOTAL - Item E1
E2 | Air Conditioning Distribution Panel 'AC' (Weatherproof)
| a) 415/240-Volts 3-phase 4-wire 18-way 150A B/B 22 kAIC |  | Item
| b) 4C x 50mm2 - to contractor's estimate |  | m
SUB-TOTAL - Item E2
E3 | Computer Distribution Panel 'CS'
| a) 208/120-Volts 3-phase 5-wire 18-way 150A B/B 14 kAIC |  | Item
| b) 3 x 50mm2 (Phase Conductors) - to contractor's estimate |  | m
| c) 1 x 95mm2 (Neutral Conductors) - to contractor's estimate |  | m
| d) 1 x 35mm2 (Ground Conductor) - to contractor's estimate |  | m
SUB-TOTAL - Item E3
E4 | Power Distribution Panel 'PS'
| a) 208/120-Volts 3-phase 4-wire 18-way 150A B/B 14 kAIC |  | Item
| b) 4 x 25mm2 - to contractor's estimate |  | m
SUB-TOTAL - Item E4
E5 | Transformers 'T1'
E5-1 | a) 'T1' - 30 kVA 3-Phase Dry Type Transformer
| 400-Volts Primary (Delta) / 208/120-Volts Secondary (Wye) | 1 | No.
| b) Primary Cable - 3C x 16mm2 - to contractor's estimate |  | m
E5-2 | a) 'T2' - 45 kVA 3-Phase Dry Type K-13 Isolation Transformer
| 400-Volts Primary (Delta) / 230/115-Volts Secondary (Wye) | 1 | No.
| b) Primary Cable - 3C x 25mm2 - to contractor's estimate |  | m
SUB-TOTAL - Item E5
To Collection $
E6 | Pre-Commissioning Testing
| a) Transformers 'T1 - T2' |  | Item
E7 | Grounding System
| a) Standby Generator |  | Item
| b) Main L.V. Panelboard and sub-distribution panels |  | Item
| d) Cable trays, supports, structured cabling bulkheads etc. |  | Item
| e) UPS units |  | Item
| f) Communications (Voice/Data) Systems |  | Item
| G) Building roof & structure |  | Item
SUB-TOTAL - Item E7
E8 | PANELS & SUB-FEEDERS
This item is to include for all contactors and associated feeder cables, all as specified on the Drawings or in the Electrical Specification. This item is also to include for all glands, clamps, supports, circuit breakers as per schedule.
E8-1 | a) Panel 'LP1' - 400/230V 3Ph 4W 42-way 150A B/B 10 kAIC |  | Item
| b) 4C x 16 mm2 X.L.P.E. - to Contractor's estimate |  | m
E8-1 | a) Panel 'LP2' - 400/230V 3Ph 4W 42-way 150A B/B 10 kAIC |  | Item
| b) 4C x 16 mm2 X.L.P.E. - to Contractor's estimate |  | m
E8-3 | a) Panel 'LP3' - 400/230V 3Ph 4W 42-way 150A B/B 10 kAIC |  | Item
| b) 4C x 16 mm2 X.L.P.E. - to Contractor's estimate |  | m
E8-4 | PANEL 'NL' - Night Lighting Panel
| 400/230-volts 3-phase 4-wire 30-way 150A B/B 10 kAIC c/w 415V 30A-3P lighting contactor, timer and local switch bank at panel |  | Item
| a) 4C x 4.0mm2 XLPE armoured - to Contractor's estimate |  | m
E8-5 | a) Panel 'P1' - 208/120V 3Ph 4W 18-way 125A B/B 10 kAIC |  | Item
| b) 4C x 6.0 mm2 X.L.P.E. - to Contractor's estimate |  | m
E8-6 | a) Panel 'P2' - 208/120V 3Ph 4W 18-way 125A B/B 10 kAIC |  | Item
| b) 4C x 6.0 mm2 X.L.P.E. - to Contractor's estimate |  | m
E8-7 | a) Panel 'P3' - 208/120V 3Ph 4W 18-way 125A B/B 10 kAIC |  | Item
| b) 4C x 6.0 mm2 X.L.P.E. - to Contractor's estimate |  | m
E8-8 | a) Panel 'C1' - 208/120V 3Ph 5W 18-way 125A B/B 10 kAIC |  | Item
| b) 3 x 50mm2 (Phase Conductors) - to contractor's estimate | 3 | m
| c) 1 x 95mm2 (Neutral Conductors) - to contractor's estimate |  | m
| d) 1 x 35mm2 (Ground Conductor) - to contractor's estimate |  | m
E8-9 | a) Panel 'C2' - 208/120V 3Ph 5W 18-way 125A B/B 10 kAIC |  | Item
| b) 3 x 10mm2 (Phase Conductors) - to contractor's estimate | 4 | m
| c) 1 x 16mm2 (Neutral Conductors) - to contractor's estimate |  | m
| d) 1 x 6.0mm2 (Ground Conductor) - to contractor's estimate |  | m
E8-10 | a) Panel 'C3' - 208/120V 3Ph 5W 18-way 125A B/B 10 kAIC |  | Item
| b) 3 x 10mm2 (Phase Conductors) - to contractor's estimate | 6 | m
| c) 1 x 16mm2 (Neutral Conductors) - to contractor's estimate |  | m
| d) 1 x 6.0mm2 (Ground Conductor) - to contractor's estimate |  | m
SUB-TOTAL - Item E8
To Collection $
E9 | AIR CONDITIONING & VENTILATION & EQUIPMENT
Weatherproof Serviceman Isolators & Cables
E9-1 | Level 1 AC Condensing Unit - 415V 50A-3P / 4C x 10mm2 XLPE (To Contractor's Estimate) | 1 | No.
E9-2 | Level 2 AC Condensing Unit - 415V 60A-3P / 4C x 16mm2 XLPE (To Contractor's Estimate) | 1 | No.
E9-3 | Level 3 AC Condensing Unit - 415V 60A-3P / 4C x 16mm2 XLPE (To Contractor's Estimate) | 1 | No.
E9-4 | Outside Air Unit - 415V 40A-3P / 4C x 6.0mm2 XLPE (To Contractor's Estimate) | 1 | No.
E9-5 | Fan Coil Units - 3C x 1.5mm2 XLPE (To Contractor's Estimate) | 35 | No.
E9-6 | Toilet Exhaust Fans - Weatherproof Isolator - 15A-2P / 3Cx1.5mm2 XLPE (To Contractor's Estimate) | 13 | No.
E9-7 | Water Heaters (Kitchen) - Weatherproof Isolator - 15A-1P / 3Cx1.5mm2 XLPE (To Contractor's Estimate) | 3 | No.
SUB-TOTAL - Item E9
E10 | Lighting Fixtures
| a) Car Park - LED fixture c/w 25'-0" steel pole | 8 | No.
| b) Security Wallpack LED fixtures | 10 | No.
| c) 2'-0" square recessed LED troffer fixture | 210 | No.
| d) 2'-0" vapourproof LED surface mount | 9 | No.
| e) 4'-0" vapourproof LED surface mount | 4 | No.
| f) Downlighters | 21 | No.
| g) Pendants | 25 | No.
| h) Emergency Exit / Emergency Lighting Combination | 8 | No.
| i) Emergency Lighting | 6 | No.
SUB-TOTAL - Item E10
E11 | Power Outlets
| a) 115-volt 15A duplex | 17 | No.
| b) 115-volt 15A duplex ground fault - | 38 | No.
| c) 115-volt 15A duplex isolated ground - | 72 | No.
| d) Combination 115-volt 15A duplex / 115-volt 15A isolated ground / communications floor outlet | 8 | No.
| e) 230-volt switched 13A duplex RCD | 17 | No.
| f) Cooktop Control switched outlet - 230V 45A | 3 | No.
| g) Hand Dryer outlet points | 10 | No.
SUB-TOTAL: Item E11
E12 | Conduit Infrastructure
| a) Fire Detection / Alarm System |  | Item
| b) Voice / Data (Communications) Outlets |  | Item
| c) Communications Steel Trunking / Basket Trays |  | Item
| d) Security System Steel Trunking / Basket Trays |  | Item
SUB-TOTAL: Item E12
To Collection $
E13 | Industrial Cable Tray / Trunking & Supports |  | Item
E14 | Lighting / Control Switches
| a) 230-volt 20A single-pole toggle - | 62 | No.
| b) 230-volt 20A two-way toggle | 6 | No.
SUB-TOTAL: Item E14
E15 | Hand Dryers | 10 | No.
Bobrick Eclipse® Dryer Model B-715E 230-Volts 1700 Watts c/w chrome cover
E16 | Conduits
This item is to include for all junction boxes, connectors, elbows,
terminations, clamps etc. - to Contractor's estimate
| a) 1/2 dia. |  | m
| b) 3/4" dia. |  | m
| c) 1" dia. |  | m
| d) Miscellaneous |  | Item
SUB-TOTAL: Item E16
E17 | Sub-Circuit Wiring
P.V.C. insulated single-core copper conductors - to Contractor's estimate
| a) 1.5mm2 |  | m
| b) 2.5mm2 |  | m
| c) 4.0mm2 |  | m
| c) 6.0mm2 |  | m
| c) 10.0mm2 |  | m
SUB-TOTAL: Item E17
E18 | MAIN L.V. CABLE DUCTS / CONNECTION
From Utility meter pillar - this item is to include for all long radius bends, fittings etc.
E18.1 | Duct connection at MUL meter Pillar roadside | 1 | item
E18.2 | 4" dia. Schedule 40 PVC L.V. ducts - to Contractor's estimate | 120 | m
E18.3 | Laying of ducts in sand beds | 1 | Item
SUB-TOTAL: Item E18
To Collection $
Collection
|  | Subtotal from |  | Pg 1
|  | Subtotal from |  | Pg 2
|  | Subtotal from |  | Pg3
|  | Subtotal from |  | Pg4
TOTAL TO MAIN BILL OF QUANTITIES

## 7.2-FSC Fire
7.2 : FIRE ALARM INSTALLATION SCHEDULE OF WORKS
Item | Description | Qty | Unit | Rate (EC$) | Amount
Contractor is to provide all materials, labour and supervision necessary to complete the Works in all respects, all as specified, shown on the Drawings or as indicated otherwise.
NOTE: All individual sub-sections of each item are to be priced in full including all Material & Labour costs.
F1 | Addressable Fire Alarm System
F1.1 | Fire Alarm Control c/w Remote Annunciators etc. | 1 | Item
F1.2 | Intelligent Multi-Sensor Smoke Detectors | 40 | No.
F1.3 | Combination Thermal / Rate-of-Rise Detectors | 3 | No.
F1.4 | Pull Stations | 4 | No.
F1.5 | Fire Alarm Sounders c/w Strobe - Internal | 4 | No.
F1.6 | Fire Alarm Sounders c/w Strobe - External | 1 | No.
F1.7 | Auxiliary Monitor Modules (to be listed in submittal) | 1 | Item
F1.8 | Auxiliary Output Modules (to be listed in submittal) | 1 | Item
SUB-TOTAL: Item F1
F2 | 4 Kg ABC Powder Fire Extinguishers ,wall mounted | 22 | No
TOTAL TO MAIN BILL OF QUANTITIES

## 7.3 FSC Plumbing
FINANCIAL SERVICES COMMISSION BUILDING
18.3 : PLUMBING INSTALLATION SCHEDULE OF WORKS
Item | Description | Qty | Unit | Rate (EC$) | Amount
Provide all materials, labour and supervision necessary to complete the Works in all respects, all as specified, shown on the Drawings or as indicated otherwise.
P1 | EXTERNAL WASTERWATER PIPING & VENT STACKS |  | Item
DWV Schedule 40 PVC - ASTM D1784/D1785/ASTM 2665 for use with push-on gasket joints (ASTM D3212) inclusive of all wastewater connections to horizontal collectors, fittings, brackets, supports etc.
P2 | TESTING |  | Item
Allow for carrying out of water pressure test on the sanitary installation to the satisfaction of the Project Architect - inclusive of verification of slopes, mirror test etc.
P3 | INTERNAL WASTERWATER PIPING |  | Item
PVC Schedule 40 DWV ASTM D1784/D1785 and fittings for use with solvent joints (D2665) - installation of wastewater and vent stacks inclusive of horizontal horizontal collectors, inclusive of all fittings, brackets, supports etc.
P4 | TESTING |  | Item
Allow for carrying out of water pressure test on the sanitary installation to the satisfaction of the Services Engineer / Project Manager - inclusive of verification of slopes, mirror test etc.
P5 | EXTERNAL POTABLE WATER RETICULATION PIPING |  | Item
Schedule 40 CPVC ASTM 1784/1785 and fittings for use with with push-on gasket joints (D3139) - installation of cold water supply lines from the MUL meter, potable pump(s) connection pipe fittings, to the building inclusive of all external works, valves etc.
P6 | External Pipe Trenches |  |  | (See BQ)
(Not Priced here -See BQ- External Works)
P7 | INTERNAL POTABLE WATER PIPING |  | Item
Schedule 40 CPVC 160 PSI ASTM D1784/D1785 and fittings for use with cement joints (D2665) - installation of the internal potable water piping connection point to the sanitary ware and appliance connections, valves, pipe fittings etc.
P8 | TESTING |  | Item
Allow for carrying out of water pressure test on the hot & cold water installation to the satisfaction of the Architect/Engineer.
To Collection
FINANCIAL SERVICES COMMISSION BUILDING- PLUMBING INSTALLATION
SCHEDULE OF WORKS (Cont'd)
Item | Description | Qty | Unit | Unit Rate | Amount
F. MISCELLANEOUS
P9 | PIPE SUPPORTS & BRACKETS | 1 | Item
P10 | HOSE BIBS C/W LOCKS | 4 | No.
P11 | WATER HEATER - A. O. Smith Model ELSF-10 230/1/60 | 3 | No.
P12 | G. APPLIANCES
Sanitary appliances and assemble and connect to all service, waste and
over-flow pipes with all necessary connectors and adaptors and plug and
screw to concrete or blockwork except otherwise described.
P12-1 | W.C. SUITES - 'S' TRAP | 10 | No.
American Standard Cadet Pro Elongated Toliet or equal approved, of white vitreous china comprising rimless washdown W.C. pan Ref: 215CA.104 with 'S' trap, seat and screws with stainless hinges, screws etc.
P12-2 | COUNTERTOP VANITY SINKS (STAFF) | 6 | No.
1-taphole washbasin American Standard Ovalyn Ref: 0495.300 or equal approved, of white vitreous china with overflow, 'S' trap, Colony Pro Single Control Lavatory Faucet
P12-3 | COUNTERTOP VANITY SINKS (EXECUTIVES) | 2 | No.
1-taphole washbasin American Standard Studio Carre´ Ref: 0426.000 or equal approved, of white vitreous china with overflow, 'S' trap, Colony Pro Single Control Lavatory Faucet
P12-4 | DISABLED WALLHUNG SINKS (DA) | 2 | No.
1-taphole washbasin American Standard Wheel Users Lavatory or equal approved, of white vitreous china with overflow, 'S' trap, Bedminister Lavatory Faucet
P12-5 | JANITOR'S STATION | 3 | No.
Concrete tiled Janitor's Station (by Main Contractor) c/w American Standard Exposed Yoke Wall-Mount Utility Faucet
P12-6 | KITCHEN SINKS (Stainless Steel Single Bowl / Single Drainboard) | 3 | No.
SUB-TOTAL - Item P12
To Collection $
FINANCIAL SERVICES COMMISSION BUILDING - PLUMBING INSTALLATION
SCHEDULE OF WORKS (Cont'd)
Item | Description | Qty | Unit | Rate | Amount
H. GENERAL
P13 | INSTALLATION OF PIPE FITINGS & CONNECTION OF SEPTIC TANK & SOAKPIT TO WASTE WATER LINE | 1 | Item
P14 | CONDENSATE WASTE PIPING | 1 | Item
Supply & install insulated refrigeration waste piping from refrigerated display cases, A/C fan coil units,connect outfalls to nearest rainwater down pipe
P15 | UTILITY METERED WATER CONNECTION CHARGE
To Collection $
Collection
|  | Subtotal from |  | Pg 1
|  | Subtotal from |  | Pg 2
|  | Subtotal from |  | Pg3
TOTAL TO MAIN BILL OF QUANTITIES

## 7.4-FSC HVAC
FINANCIAL SERVICES COMMISSION BUILDING
7.4 : HVAC INSTALLATION SCHEDULE OF WORKS
Item | Description | Qty | Unit | Rate (EC$) | Amount
AIR CONDITIONING
A1 | LEVEL 1
A1.1 | Indoor Fan Coil Units
a | Senior Officers - FCU 1.1
| FDT36KXZE1 12,283 Btu/hr Multi Flow Cassette, 220V/1Ph/60Hz | 1 | No.
b | Kitchen/ Lunch Room - FCU 1.2
| FDK22KXZE1 7,506 Btu/hr High Wall Mounted, 220V/1Ph/60Hz | 1 | No.
c | Storage Room - FCU 1.3
| FDK15KXZE1 5,120 Btu/hr High Wall Mounted, 220V/1Ph/60Hz | 1 | No.
d | Junior Officers - FCU 1.4
| FDU112KXE6F 38,215 Btu/hr Ceiling Concealed Mounted FCU, 220V/1Ph/60Hz | 1 | No.
e | Interview 1 - FCU 1.5
| FDK36KXZE1 12,283 Btu/hr High Wall Mounted, 220V/1Ph/60Hz | 1 | No.
f | Interview 2 - FCU 1.6
| FDK36KXZE1 12,283 Btu/hr High Wall Mounted, 220V/1Ph/60Hz | 1 | No.
g | Senior Officer - FCU 1.7
| FDT28KXZE1 9,554 Btu/hr Multi Flow Cassette, 220V/1Ph/60Hz | 1 | No.
h | Storage Room 2 - FCU 1.8
| FDK15KXZE1 5,120 Btu/hr High Wall Mounted, 220V/1Ph/60Hz | 1 | No.
i | Server Room - FCU 1.9
| FDK15KXZE1 5,120 Btu/hr High Wall Mounted, 220V/1Ph/60Hz | 1 | No.
j | Big Hall - FCU 1.10
| FDU90KXE6F 24,226 Btu/hr Ceiling Concealed Mounted FCU, 220V/1Ph/60Hz | 1 | No.
k | FSC Archives - FCU 1.11
| FDK36KXZE1 12,283 Btu/hr High Wall Mounted, 220V/1Ph/60Hz | 1 | No.
l | L.V Electrical Room - FCU 1.2
| FDK22KXZE1 7,506 Btu/hr High Wall Mounted, 220V/1Ph/60Hz | 1 | No.
A1.2 | Condensing Units
a | FDC450KXZE1 16H.P Mitsubishi VRF Multi Condensing Unit, 400V/3Ph/60Hz | 1 | No.
A1.3 | Supply Air Diffusers
a | Supply Grilles: Type 1 - AIRGUIDE JS-PLT-4 12"x 12"/24"x24", 160-260 cfm, 10" flex connection |  | Item
A1.4 | Return Air Grilles
a | Return Grilles: AIRGUIDE RA-T 24"x 24" Return Air Grilles |  | Item
A1.5 | Supply air ducting - c/w 1.5" External Insulation and internal liner up to 6 ft from unit connection |  | Item
A1.6 | Return air ducting - c/w 1.0" thick Internal acoustic insulation / liner 12 feet from unit / 1.5" External Insulation |  | Item
A1.7 | Flexible ducting - as indicated on Drawing AC-02 |  | Item
A1.8 | Voltage Monitor - Motor Saver Model 300 or Watsco EAC 801 or approved equal. |  | Item
A1.9 | Thermostats & Controls as on the Dwgs & Specified C/w remote sensor & lockable tamper proof case |  | Item
A1.10 | Vibration Isolators for Condensing Units |  | Item
A1.11 | Fire dampers: GREENHECK DFD - Type B installed in Supply duct & Return penetrations |  | Item
Sub Total -To Collection $
Item | Description | Qty | Unit | Rate (EC$) | Amount
A2 | LEVEL 2
A2.1 | Indoor Fan Coil Units
a | FSC Commissioner - FCU 2.1
| FDT45KXZE1 15,354 Btu/hr Multi Flow Cassette, 220V/1Ph/60Hz | 1 | No.
b | Library/ Training Room - FCU 2.2
| FDT56KXZE1 19,107 Btu/hr Multi Flow Cassette, 220V/1Ph/60Hz | 1 | No.
c | Conference Room - FCU 2.3
| FDT71KXZE1 24,226 Btu/hr Multi Flow Cassette, 220V/1Ph/60Hz | 1 | No.
d | FSC Main Office - FCU 2.4
| FDU280KXZE1 95,539 Btu/hr Ceiling Concealed Mounted FCU, 220V/1Ph/60Hz | 1 | No.
e | Electrical &Server Room - FCU 2.5
| FDK15KXZE1 5,120 Btu/hr High Wall Mounted, 220V/1Ph/60Hz | 1 | No.
f | Lobby & DA Meeting Room - FCU 2.6
| FDU90KXE6F 24,226 Btu/hr Ceiling Concealed Mounted FCU, 220V/1Ph/60Hz | 1 | No.
g | IP & CO Filing - FCU 2.7
| FDK28KXZE1 9,554 Btu/hr High Wall Mounted, 220V/1Ph/60Hz | 1 | No.
h | FSC Filing - FCU 2.8, 2.9
| FDK36KXZE1 12,283 Btu/hr High Wall Mounted, 220V/1Ph/60Hz | 2 | No.
i | Hall - FCU 2.10
| FDUM36KXE6F 12,283 Btu/hr Ceiling Concealed Mounted FCU, 220V/1Ph/60Hz | 1 | No.
j | Kitchen - FCU 2.11
| FDK28KXZE1 9,554 Btu/hr High Wall Mounted, 220V/1Ph/60Hz | 1 | No.
A2.2 | Condensing Units
a | First Floor
External Condensing Unit - CU 2.1
| FDC670KXZE1 24H.P Mitsubishi VRF Multi Condensing Unit, 400V/3Ph/60Hz | 1 | No.
A2.3 | Supply Air Diffusers
a | Supply Grilles: Type 1 - AIRGUIDE JS-PLT-4 12"x 12"/24"x24", 160-260 cfm, 10" flex connection |  | Item
A2.4 | Return Air Grilles
a | Return Grilles: AIRGUIDE RA-T 24"x 24" Return Air Grilles |  | Item
A2.5 | Supply air ducting - c/w 1.5" External Insulation and internal liner up to 6 ft from unit connection |  | Item
A2.6 | Return air ducting - c/w 1.0" thick Internal acoustic insulation / liner 12 feet from unit / 1.5" External Insulation |  | Item
A2.7 | Flexible ducting - as indicated on Drawing AC-03 |  | Item
A2.8 | Voltage Monitor - Motor Saver Model 300 or Watsco EAC 801 or approved equal. |  | Item
A2.9 | Thermostats & Controls as shown on the Drawings and Specified C/w remote sensor & lockable tamper proof case |  | Item
A2.10 | Vibration Isolators for Condensing Units |  | Item
A2.11 | Fire dampers: GREENHECK DFD - Type B installed in Supply duct & Return penetrations |  | Item
| Sub Total -To Collection $ |  |  | $
Item | Description | Qty | Unit | Rate (EC$) | Amount
A3 | LEVEL 3
A3.1 | Indoor Fan Coil Units
a | Audtitor General - FCU 3.1
| FDT56KXZE1 19,107 Btu/hr Multi Flow Cassette, 220V/1Ph/60Hz | 1 | No.
b | Dep. Auditor - FCU 3.2
| FDT45KXZE1 15,354 Btu/hr Multi Flow Cassette, 220V/1Ph/60Hz | 1 | No.
c | Library - FCU 3.3
| FDT56KXZE1 19,107 Btu/hr Multi Flow Cassette, 220V/1Ph/60Hz | 1 | No.
d | Audit Main Floor - FCU 3.4
| FDU280KXZE1 95,539 Btu/hr Ceiling Concealed Mounted FCU, 220V/1Ph/60Hz | 1 | No.
e | Server Room - FCU 3.5
| FDK15KXZE1 5,120 Btu/hr High Wall Mounted, 220V/1Ph/60Hz | 1 | No.
f | Telecom/ Elec Room - FCU 3.6
| FDK15KXZE1 5,120 Btu/hr High Wall Mounted, 220V/1Ph/60Hz | 1 | No.
g | Lobby - FCU 3.7
| FDU112KXE6F 38,215 Btu/hr Ceiling Concealed Mounted FCU, 220V/1Ph/60Hz | 1 | No.
h | Filing - FCU 3.8
| FDK36KXZE1 12,283 Btu/hr High Wall Mounted, 220V/1Ph/60Hz | 1 | No.
i | Hall - FCU 3.9
| FDUM28KXE6F 9,556 Btu/hr Ceiling Concealed Mounted FCU, 220V/1Ph/60Hz | 1 | No.
j | Kitchen - FCU 3.10
| FDK36KXZE1 12,283 Btu/hr High Wall Mounted, 220V/1Ph/60Hz | 1 | No.
A3.2 | Condensing Units
a | Second Floor
External Condensing Unit - CU 3.1
| FDC670KXZE1 24H.P Mitsubishi VRF Multi Condensing Unit, 400V/3Ph/60Hz | 1 | No.
A3.3 | Supply Air Diffusers
a | Supply Grilles: Type 1 - AIRGUIDE JS-PLT-4 12"x 12"/24"x24", 160-260 cfm, 10" flex connection |  | Item
A3.4 | Return Air Grilles
a | Return Grilles: AIRGUIDE RA-T 24"x 24" Return Air Grilles |  | Item
A3.5 | Supply air ducting - c/w 1.5" External Insulation and internal liner up to 6 ft from unit connection |  | Item
A3.6 | Return air ducting - c/w 1.0" thick Internal acoustic insulation / liner 12 feet from unit / 1.5" External Insulation |  | Item
A3.7 | Flexible ducting - as indicated on Drawing AC-04 |  | Item
A3.8 | Voltage Monitor - Motor Saver Model 300 or Watsco EAC 801 or approved equal. |  | Item
A3.9 | Thermostats & Controls as shown on the Drawings and Specified C/w remote sensor & lockable tamper proof case |  | Item
A3.10 | Vibration Isolators for Condensing Units |  | Item
A3.11 | Fire dampers: GREENHECK DFD - Type B installed in Supply duct & Return penetrations |  | Item
| Sub Total -To Collection $ |  |  | $
Item | Description | Qty | Unit | Rate (EC$) | Amount
A4 | Outside Air Processing System
A4.1 | Outside Air Processing Fan Coil Units
a | Level 1
| FDU650FKXZE1 388 cfm Ceiling Concealed Outside Air FCU c/w duct work, grilles, flexible ducting, filters incl. of rack & outside air louver 220V/1Ph/60Hz | 1 | No.
b | Level 2
| FDU650FKXZE1 388 cfm Ceiling Concealed Outside Air FCU c/w duct work, grilles, flexible ducting, filters incl. of rack & outside air louver 220V/1Ph/60Hz | 1 | No.
c | Level 3
| FDU650FKXZE1 388 cfm Ceiling Concealed Outside Air FCU c/w duct work, grilles, flexible ducting, filters incl. of rack & outside air louver 220V/1Ph/60Hz | 1 | No.
A4.2 | Condensing Units
a | Ground, First & Second Floor Condensing Unit
External Condensing Unit - CU 4.1
| FDC280KXE6M 8H.P Mitsubishi VRF Multi Condensing Unit, 220V/3Ph/60Hz | 1 | No.
A4.3 | Supply Air Diffusers
a | Supply Grilles: Type 2 - AIRGUIDE JS-PLT-4 8"x 8"/24"x24", 35-85 cfm, 6-8" flex connection |  | Item
A4.4 | Supply air ducting - c/w 1.5" External Insulation and internal liner up to 6 ft from unit connection |  | Item
A4.5 | Flexible ducting - as indicated on Drawing AC-02, AC-03 & AC-04 |  | Item
A4.6 | Voltage Monitor - Motor Saver Model 300 or Watsco EAC 801 or approved equal. | 1 | No.
A4.7 | Thermostats & Controls as shown on the Drawings and Specified C/w remote sensor & lockable tamper proof case | 3 | No.
A4.8 | Vibration Isolators for Condensing Units |  | Item
A4.9 | Fire dampers: GREENHECK DFD - Type B installed in Supply duct & Return penetrations |  | Item
ST 4 | Sub Total -To Collection $ |  |  | $
Item | Description | Qty | Unit | Rate (EC$) | Amount
A5 | VENTILATION
A5.1 | Level 1
a | Male Washroom
| Xpelair XID-100 Inline Exhaust Fan c/w sheet metal ductwork, 8"x8" RA Grilles, 230V/1Ph/60Hz | 1 | No.
(Fan to be switched with lights)
b | Female Washroom
| Xpelair XID-100 Inline Exhaust Fan c/w sheet metal ductwork, 8"x8" RA Grilles, 230V/1Ph/60Hz | 1 | No.
(Fan to be switched with lights)
c | Kitchen/ Lunch Room
| Xpelair GX-6 Wall Mounted Exhaust Fan, 230V/1Ph/60Hz | 1 | No.
(Fan to be independently switched)
A5.2 | Level 2
a | FSC Commissioner Washroom
| Xpelair XID-100 Inline Exhaust Fan c/w sheet metal ductwork, 8"x8" RA Grilles, 230V/1Ph/60Hz | 1 | No.
(Fan to be switched with lights)
b | DA Washroom
| Xpelair XID-100 Inline Exhaust Fan c/w sheet metal ductwork, 8"x8" RA Grilles, 230V/1Ph/60Hz | 1 | No.
(Fan to be switched with lights)
c | Male Washroom
| Xpelair XID-100 Inline Exhaust Fan c/w sheet metal ductwork, 8"x8" RA Grilles, 230V/1Ph/60Hz | 1 | No.
(Fan to be switched with lights)
d | Female Washroom
| Xpelair XID-100 Inline Exhaust Fan c/w sheet metal ductwork, 8"x8" RA Grilles, 230V/1Ph/60Hz | 1 | No.
(Fan to be switched with lights)
e | Kitchen
| Xpelair GX-6 Wall Mounted Exhaust Fan, 230V/1Ph/60Hz | 1 | No.
(Fan to be independently switched)
f | Electrical Room/ Server Room
| Xpelair GX-6 Wall Mounted Exhaust Fan, 230V/1Ph/60Hz | 1 | No.
(Fan to be independently switched)
A5.2 | Level 3
a | Auditor General Washroom
| Xpelair XID-100 Inline Exhaust Fan c/w sheet metal ductwork, 8"x8" RA Grilles, 230V/1Ph/60Hz | 1 | No.
(Fan to be switched with lights)
b | DA Washroom
| Xpelair XID-100 Inline Exhaust Fan c/w sheet metal ductwork, 8"x8" RA Grilles, 230V/1Ph/60Hz | 1 | No.
(Fan to be switched with lights)
c | Male Washroom
| Xpelair XID-100 Inline Exhaust Fan c/w sheet metal ductwork, 8"x8" RA Grilles, 230V/1Ph/60Hz | 1 | No.
(Fan to be switched with lights)
d | Female Washroom
| Xpelair XID-100 Inline Exhaust Fan c/w sheet metal ductwork, 8"x8" RA Grilles, 230V/1Ph/60Hz | 1 | No.
(Fan to be switched with lights)
e | Kitchen
| Xpelair GX-6 Wall Mounted Exhaust Fan, 230V/1Ph/60Hz | 1 | No.
(Fan to be independently switched)
Sub Total -To Collection $
Item | Description | Qty | Unit | Rate (EC$) | Amount
A6 | A/C Equipment Stands & Supports - This item is to include for all trays, supports, hilti rods, brackets, etc. associated with the suspension & support of all ducting, piping and equipment |  | Item
A7 | FIRE STOPPING - This item is to include for the firestopping of all service penetrations through floors U.L. / NFPA approved sealing (foam) compound.- the A/C Contractor is to allow in his pricing for Specificed Technologies Inc. - SpecSeal or approved equal |  | Item
A8 | Inspections, Testing & Commissioning |  | Item
A9 | Provide for Craneage &/or Transport |  | Item
A10 | Project management - Provide for suitably qualified representative of “Project Engineer” status as outlined in the Specification |  | Item
A11 | Miscellaneous and all other matters-To cater for items not included above but necessary to complete the Works |  | Item
A12 | Balancing Report |  | Item
A13 | Service Contract - Provide for twelve (12) month Service Contract as outlined in the specifications |  | Item
Sub Total -To Collection $
Collection
|  | Subtotal from |  | Pg 1
|  | Subtotal from |  | Pg 2
|  | Subtotal from |  | Pg3
|  | Subtotal from |  | Pg4
|  | Subtotal from |  | Pg 5
|  | Subtotal from |  | Pg 6
TOTAL TO MAIN BILL OF QUANTITIES