## 8.0 Optional Works
Financial Services Commission Bldg-Little Bay 8.0: OPTIONAL WORKS (For quotations only)
NB: These optional works are for quotation of cost only and shall not to be included in the contract price stated on the Form of Tender.These options may be later applied to the contract works in a variation order.
A | Supply and install platform wheel chair lift by Bruno with load capacity of 750 Lbs. as per Particular/Material Specification | Item
B | Supply, fit and fix Casino architectural cable railing systems by Trex Commercial Products as per the particular/material specifications | 12 | LY
C | 100Kw/125KVA standby generator and automatic transfer switch. Simmilar to the Genertor described in the Materials Specifications | 1 | No.
D | Supply & Instll 4C x 95 cable connections for 100 Kw standby generator | Item
E | Supply & Install the optional modified Distribution Panel described in the section 8.2 Panel Schedule labeld 'M' Modified, to accommodate the above 100kw stand by generator and the digital smart meter described below | Item
F | Smart Sub Metering : Supply & install Shark MP200 Multi-Point multifunctioning power & energy metering system to all circuits in modified Panel' M' (See section 8.2). Unit to be supplied along with supporting Energy Reporter EXT software, all as described in the Material Specifications | Item
G | Provide for separate floor by floor electric metering: Insert the net total from the section 8.1 Optional Works-Separate Electrical Metering-Schedule of Work | Item
Signed: |  |  |  | Date:
Tenderer's Authorized Signatory

## 8.1 Optional Works-Metering
Financial Services Commission Bldg-Little Bay 8.1: Optional Works-Separate Electrical Metering
NB: These optional works are for quotation of cost only and shall not to be included in the contract price stated on the form of Tender.These changes may be later applied to the contract works in a variation order. This schedule includes items of work which the Bidder priced in the Measured Works that shall be substracted from the Contract works if a variation order for Separate Metering is issued by the Architect. This Schedule of works is based on the optional elctrical meter network described in the attached schematic diagram in Part B Section 8.3.
Item | Description | Qty | Unit | Rate | Total
WORKS TO BE SUBSTRACTED
E1 | a) 415V 400A 3-Pole 22 kAIC Main Utility L.V. Isolator | -1 | Item
| b) Automatic Transfer Switch - ASCO 300 (or equal aproved) 415V 400A 3-pole 22 kAIC | -1 | Item
c) 4C x 240mm2 X.L.P.E. Generator Cables- to Contractor's Estimate
| 1. Utiliy Main to main Isolator and to ATS | -50 | m
| 2. Generator to Generator Main Isolator and ATS |  | m
| 3. ATS to Main Panel 'M' | -2
| e) Main L.V. Distribution Panel 'M' - 415/240V 3-Phase 4-Wire 30-Way 400A B/B 22 kAIC c/w Digital Power Meter, CT.s, Ground Fault and 250 kA TVSS and all branch circuit breakers | -1 | Item
| f) Cable Trays, ducts, supports etc. |  | Item
E2 | Air Conditioning Distribution Panel 'AC' (Weatherproof)
| a) 415/240-Volts 3-phase 4-wire 18-way 150A B/B 22 kAIC | -1 | Item
| b) 4C x 50mm2 - to contractor's estimate | -20 | m
E3 | Computer Distribution Panel 'CS'
| a) 208/120-Volts 3-phase 5-wire 18-way 150A B/B 14 kAIC | -1 | Item
| b) 3 x 50mm2 (Phase Conductors) - to contractor's estimate | -3 | m
| c) 1 x 95mm2 (Neutral Conductors) - to contractor's estimate | -3 | m
| d) 1 x 35mm2 (Ground Conductor) - to contractor's estimate | -3 | m
E4 | Power Distribution Panel 'PS'
| a) 208/120-Volts 3-phase 4-wire 18-way 150A B/B 14 kAIC | -1 | Item
| b) 4 x 25mm2 - to contractor's estimate | -3 | m
E5 | Transformers 'T1'
E5-1 | a) 'T1' - 30 kVA 3-Phase Dry Type Transformer | -1
| 400-Volts Primary (Delta) / 208/120-Volts Secondary (Wye) |  | No.
| b) Primary Cable - 3C x 16mm2 - to contractor's estimate | -3 | m
E5-2 | a) 'T2' - 45 kVA 3-Phase Dry Type K-13 Isolation Transformer | -1
| 400-Volts Primary (Delta) / 230/115-Volts Secondary (Wye) |  | No.
| b) Primary Cable - 3C x 25mm2 - to contractor's estimate | -3 | m
TOTAL AMOUNT OF SUBTRACTIONS
Item | Description | Qty | Unit | Rate | Total
ADDITIONS
| 3 Module 3 Phase Meter Stack | 1 | ea
Additions for Level 1:
| Mains Isolator - Level 1 , 150A, 3 Pole, 400/230V | 1 | ea
| Automatic Transfer Switch - ASCO 300 (or equal aproved) 415V 150A 3-pole 22 kAIC (Level 1) | 1
Distribution Panel M1
| a) 400/230-Volts 3-phase 4-wire 18-way 250A B/B 14 kAIC | 1 | ea
| b) 70mm2 4 core - to contractor's estimate | 50 | m
| c) 250KA TVSS | 1 | ea
| d) 16mm2 4 core cable to condensing Unit Level 1 | 20 | m
Transformer 'T11' (To Supply DP P1)
| a) 'T1' - 10 kVA 3-Phase Dry Type Transformer | 1 | ea
400-Volts Primary (Delta) / 208/120-Volts Secondary (Wye)
| b) 4 x 10mm2 - to contractor's estimate | 3 | m
| a) 'T12' - 10 kVA 3-Phase Dry Type K-13 Isolation Transformer | 1 | ea
400-Volts Primary (Delta) / 230/115-Volts Secondary (Wye)
| b) 3 x 10mm2 (Phase Conductors) - to contractor's estimate | 4 | m
| c) 1 x 16mm2 (Neutral Conductors) - to contractor's estimate | 4 | m
| d) 1 x 16mm2 (Ground Conductor) - to contractor's estimate | 4 | m
Additions for Level 2:
| Mains Isolator - Level 2 , 150A, 3 Pole, 400/230V | 1 | ea
| Automatic Transfer Switch - ASCO 300 (or equal aproved) 415V 150A 3-pole 22 kAIC (Level 2) | 1 | ea
Distribution Panel M2
| a) 400/230-Volts 3-phase 4-wire 30-way 250A B/B 14 kAIC | 1 | ea
| b) 95mm2 4 core cable | 50 | m
| c) 250KA TVSS | 1 | ea
| d) 25mm2 4 core cable to condensing Unit Level 2 | 25 | m
| e) 16mm2 4 core cable to DOAS condensing Unit | 25 | m
Transformer 'T21' (To Supply DP P2)
| a) 'T21' - 10 kVA 3-Phase Dry Type Transformer | 1 | ea
400-Volts Primary (Delta) / 208/120-Volts Secondary (Wye)
| b) 4 x 10mm2 - to contractor's estimate | 3 | m
Transformer 'T22 (To Supply DP C2)
| a) 'T22' - 15kVA 3-Phase Dry Type K-13 Isolation Transformer | 1 | ea
400-Volts Primary (Delta) / 230/115-Volts Secondary (Wye)
| b) 3 x 10mm2 (Phase Conductors) - to contractor's estimate | 4 | m
| c) 1 x 16mm2 (Neutral Conductors) - to contractor's estimate | 4 | m
| d) 1 x 16mm2 (Ground Conductor) - to contractor's estimate | 4 | m
SUB-TOTAL-ADDITIONAL WORKS
Item | Description | Qty | Unit | Rate | Total
Additions for Level 3:
| Mains Isolator - Level 2 , 150A, 3 Pole, 400/230V | 1 | ea
| Automatic Transfer Switch - ASCO 300 (or equal aproved) 415V 150A 3-pole 22 kAIC (Level 2) | 1 | ea
Distribution Panel M3
| a) 400/230-Volts 3-phase 4-wire 18-way 250A B/B 14 kAIC | 1 | ea
| b) 95mm2 4 core cable | 50 | m
| c) 250KA TVSS | 1 | ea
| d) 25mm2 4 core cable to condensing Unit Level 3 | 25 | m |  | 6
Transformer 'T31' (To Supply DP P3)
| a) 'T31' - 10 kVA 3-Phase Dry Type Transformer | 1 | ea
400-Volts Primary (Delta) / 208/120-Volts Secondary (Wye)
| b) 4 x 10mm2 - to contractor's estimate | 4 | m
Transformer 'T32 (To Supply DP C3)
| a) 'T32' - 15kVA 3-Phase Dry Type K-13 Isolation Transformer | 1 | ea
400-Volts Primary (Delta) / 230/115-Volts Secondary (Wye)
| b) 3 x 10mm2 (Phase Conductors) - to contractor's estimate | 4 | m
| c) 1 x 16mm2 (Neutral Conductors) - to contractor's estimate | 4 | m
| d) 1 x 16mm2 (Ground Conductor) - to contractor's estimate | 4 | m
| Generator Distribution Panel G1 - 415/240V 3-Phase 4-Wire 12-Way 400A B/B | 1 | ea
SUB-TOTAL-ADDITIONAL WORKS
TOTAL-ADDITIONAL WORKS
SUMMARY OF ADDITIONS & SUBTRACTIONS
TOTAL AMOUNT OF SUBTRACTIONS
TOTAL COST OF ADDITIONAL WORKS
8.1 NET AMOUNT CARRIED TO 8.0 OPTIONAL WORKS